## Cover
CABLE SURVEY REPORT · SS-2026-SAMPLE
AS-BUILT CABLE DOCUMENTATION
Low-Voltage Field Survey
Sample Loft Office
123 West Sample Street, New York, NY
PROJECT METADATA
| SURVEY DATE | October 8, 2026
| PROJECT NO. | SS-2026-SAMPLE
| SURVEYED BY | Field Survey Team
| CLIENT CONTACT | Client details redacted
| TOTAL CABLES | 57 cables across 1 floor
PREPARED BY
Seneca Security Inc.
244 Fifth Avenue, Suite 2605, New York, NY 10001
| PHONE | 212-347-5400
| EMAIL | info@senecasecurity.com
Seneca Security Inc. · Generated October 15, 2026

## Summary
Executive Summary
Sample Loft Office — 123 West Sample Street, New York, NY
57 TOTAL CABLES 1 floor surveyed |  | 3,524 LINEAR FEET avg 63 ft per run · 56 of 57 measured | 77% PASS RATE 44 pass · 11 fail · 2 untested
Cable Inventory by Type
Type | Count | Distribution | Share
Data (Cat5/5e/6) | 26 | 26 | 45.61%
Coax (RG6/RG59) | 6 | 6 | 10.53%
Speaker | 8 | 8 | 14.04%
Security Camera | 8 | 8 | 14.04%
Telephone | 7 | 7 | 12.28%
Unknown | 2 | 2 | 3.509%
Test Results
Result | Count | Distribution | Share
Pass | 44 | 44 | 77.19%
Fail | 11 | 11 | 19.3%
Untested | 2 | 2 | 3.509%
Deficiencies — Failed Tests (11)
Cable ID | Floor | Location | Test Notes
DATA-02 | Seventh Floor | Conference (Hudson) | Shorted pair 3-6. Floor box damaged
SPKR-02 | Seventh Floor | Conference (Hudson) | Open circuit
COAX-02 | Seventh Floor | Office 1 | Dead
UNK-01 | Seventh Floor | Open Workspace North | Abandoned. Cut at ceiling
DATA-10 | Seventh Floor | Open Workspace North | Open pair 4-5
DATA-11 | Seventh Floor | Open Workspace North | Not found at head-end
COAX-03 | Seventh Floor | Café | Dead. No signal at TV
CAM-07 | Seventh Floor | Reception | No PoE at camera end
DATA-20 | Seventh Floor | Open Workspace South | Split pair. Fails Cat6
COAX-05 | Seventh Floor | Executive Office | Dead
TEL-07 | Seventh Floor | Office 2 | No dial tone. Pair broken at 66 block

## Master Schedule
Sample Loft Office — Master Schedule
57 cables · Sample Loft Office · Generated October 15, 2026
# | Cable ID | Floor | Type | Room / Location | Head-End Port | Len (ft) | Test | Test Notes | Notes | Photos
01 | CAM-01 | Seventh Floor | CAMERA | Open Workspace North | NVR, Port 1 | 89 | PASS | PoE OK | Covers workspace from rear
02 | CAM-02 | Seventh Floor | CAMERA | Open Workspace North | NVR, Port 2 | 58 | PASS | PoE OK | Covers workspace toward core
03 | CAM-03 | Seventh Floor | CAMERA | Corridor | NVR, Port 3 | 55 | PASS | PoE OK | Looks down corridor to reception
04 | CAM-04 | Seventh Floor | CAMERA | Stair A | NVR, Port 4 | 57 | PASS | PoE OK | Stair door
05 | CAM-05 | Seventh Floor | CAMERA | IT / MDF | NVR, Port 5 | 31 | PASS | PoE OK | Rack room camera
06 | CAM-06 | Seventh Floor | CAMERA | Reception | NVR, Port 6 | 48 | PASS | PoE OK | Entry camera
07 | CAM-07 | Seventh Floor | CAMERA | Reception | NVR, Port 7 | 43 | FAIL | No PoE at camera end | Covers reception desk
08 | CAM-08 | Seventh Floor | CAMERA | Open Workspace South | NVR, Port 8 | 47 | PASS | PoE OK | Covers workspace from core
01 | COAX-01 | Seventh Floor | COAX | Conference (Hudson) | IT Room Rack B, Coax Splitter Port 1 | 95 | PASS |  | Display feed
02 | COAX-02 | Seventh Floor | COAX | Office 1 | IT Room Rack B, Coax Splitter Port 2 | 82 | FAIL | Dead | Abandoned TV outlet
03 | COAX-03 | Seventh Floor | COAX | Café | IT Room Rack B, Coax Splitter Port 3 | 64 | FAIL | Dead. No signal at TV | TV wall
04 | COAX-04 | Seventh Floor | COAX | Reception | IT Room Rack B, Coax Splitter Port 4 | 38 | PASS |  | Lobby TV, logo wall
05 | COAX-05 | Seventh Floor | COAX | Executive Office | IT Room Rack B, Coax Splitter Port 5 | 54 | FAIL | Dead | TV wall
06 | COAX-06 | Seventh Floor | COAX | Office 2 | IT Room Rack B, Coax Splitter Port 6 | 55 | PASS |  | TV wall
01 | DATA-01 | Seventh Floor | DATA | Conference (Hudson) | IT Room Rack A, PP1-01 | 89 | PASS | Cat6 certified | Wall plate behind display
02 | DATA-02 | Seventh Floor | DATA | Conference (Hudson) | IT Room Rack A, PP1-02 | 98 | FAIL | Shorted pair 3-6. Floor box damaged | Floor box under table
03 | DATA-03 | Seventh Floor | DATA | Conference (Hudson) | IT Room Rack A, PP1-03 | 84 | PASS | Cat6 certified | Wall plate, display wall
04 | DATA-04 | Seventh Floor | DATA | Office 1 | IT Room Rack A, PP1-04 | 92 | PASS |  | Desk wall
05 | DATA-05 | Seventh Floor | DATA | Office 1 | IT Room Rack A, PP1-05 | 78 | PASS | Continuity OK. Not terminated | Near door
06 | DATA-06 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-06 | 92 | PASS |  | Pod A
07 | DATA-07 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-07 | 78 | PASS |  | Pod A
08 | DATA-08 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-08 | 83 | PASS |  | Pod B
09 | DATA-09 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-09 | 74 | PASS |  | Pod B
10 | DATA-10 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-10 | 74 | FAIL | Open pair 4-5 | Pod C
11 | DATA-11 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-11 | 71 | FAIL | Not found at head-end | Pod C
12 | DATA-12 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-12 | 64 | PASS |  | Pod D
13 | DATA-13 | Seventh Floor | DATA | Open Workspace North | IT Room Rack A, PP1-13 | 56 | PASS |  | Pod D
14 | DATA-14 | Seventh Floor | DATA | Café | IT Room Rack A, PP1-14 | 69 | PASS |  | Counter, coffee machine telemetry
15 | DATA-15 | Seventh Floor | DATA | Reception | IT Room Rack A, PP1-15 | 41 | PASS | Cat6 certified | Access control reader, glass doors
16 | DATA-16 | Seventh Floor | DATA | Reception | IT Room Rack A, PP1-16 | 42 | PASS |  | Wall plate behind sofa
17 | DATA-17 | Seventh Floor | DATA | Reception | IT Room Rack A, PP1-17 | 46 | PASS |  | Reception desk
18 | DATA-18 | Seventh Floor | DATA | Open Workspace South | IT Room Rack A, PP1-18 | 55 | PASS |  | Pod E
19 | DATA-19 | Seventh Floor | DATA | Open Workspace South | IT Room Rack A, PP1-19 | 41 | PASS | Continuity OK. Not terminated | Between pods
20 | DATA-20 | Seventh Floor | DATA | Open Workspace South | IT Room Rack A, PP1-20 | 39 | FAIL | Split pair. Fails Cat6 | Pod F
21 | DATA-21 | Seventh Floor | DATA | Phone Booth 1 | IT Room Rack A, PP1-21 | 36 | PASS
22 | DATA-22 | Seventh Floor | DATA | Phone Booth 2 | IT Room Rack A, PP1-22 | 47 | UNTESTED | Booth locked. No access
23 | DATA-23 | Seventh Floor | DATA | Executive Office | IT Room Rack A, PP1-23 | 72 | PASS | Cat6 certified | Desk wall
24 | DATA-24 | Seventh Floor | DATA | Executive Office | IT Room Rack A, PP1-24 | 56 | PASS |  | Credenza
25 | DATA-25 | Seventh Floor | DATA | Office 2 | IT Room Rack A, PP1-25 | 62 | PASS |  | Desk wall
26 | DATA-26 | Seventh Floor | DATA | Office 2 | IT Room Rack A, PP1-26 | 54 | PASS |  | Window wall
01 | SPKR-01 | Seventh Floor | SPEAKER | Conference (Hudson) | IT Room Rack B, Amp Zone N | 101 | PASS |  | Ceiling speaker, left
02 | SPKR-02 | Seventh Floor | SPEAKER | Conference (Hudson) | IT Room Rack B, Amp Zone N | 90 | FAIL | Open circuit | Ceiling speaker, right
03 | SPKR-03 | Seventh Floor | SPEAKER | Open Workspace North | IT Room Rack B, Amp Zone N | 76 | PASS |  | Ceiling, paging zone N
04 | SPKR-04 | Seventh Floor | SPEAKER | Open Workspace North | IT Room Rack B, Amp Zone N | 68 | PASS |  | Ceiling, paging zone N
05 | SPKR-05 | Seventh Floor | SPEAKER | Café | IT Room Rack B, Amp Zone S | 53 | PASS |  | Ceiling
06 | SPKR-06 | Seventh Floor | SPEAKER | Reception | IT Room Rack B, Amp Zone S | 33 | PASS |  | Ceiling, background music
07 | SPKR-07 | Seventh Floor | SPEAKER | Open Workspace South | IT Room Rack B, Amp Zone S | 40 | PASS |  | Ceiling, paging zone S
08 | SPKR-08 | Seventh Floor | SPEAKER | Executive Office | IT Room Rack B, Amp Zone S | 58 | PASS |  | Ceiling
01 | TEL-01 | Seventh Floor | PHONE | Conference (Hudson) | 66 Block, Pair 1 | 104 | PASS |  | Conference phone
02 | TEL-02 | Seventh Floor | PHONE | Office 1 | 66 Block, Pair 2 | 91 | PASS
03 | TEL-03 | Seventh Floor | PHONE | Stair A | 66 Block, Pair 3 | 46 | PASS | Dial tone OK | Area of refuge phone
04 | TEL-04 | Seventh Floor | PHONE | Elevator | 66 Block, Pair 4 | 30 | PASS | Dial tone OK | Elevator emergency line
05 | TEL-05 | Seventh Floor | PHONE | Reception | 66 Block, Pair 5 | 38 | PASS |  | Reception desk
06 | TEL-06 | Seventh Floor | PHONE | Executive Office | 66 Block, Pair 6 | 72 | PASS
07 | TEL-07 | Seventh Floor | PHONE | Office 2 | 66 Block, Pair 7 | 46 | FAIL | No dial tone. Pair broken at 66 block
01 | UNK-01 | Seventh Floor | UNKNOWN | Open Workspace North |  | 69 | FAIL | Abandoned. Cut at ceiling | Unlabeled gray cable
02 | UNK-02 | Seventh Floor | UNKNOWN | ELEC |  |  | UNTESTED | Could not trace. Terminates in panel | Unlabeled, ELEC closet

## Seventh Floor
Seventh Floor — Cable Schedule
57 cables · Sample Loft Office · Generated October 15, 2026
# | Cable ID | Type | Room / Location | Head-End Port | Len (ft) | Test | Test Notes | Notes | Photos
01 | CAM-01 | CAMERA | Open Workspace North | NVR, Port 1 | 89 | PASS | PoE OK | Covers workspace from rear
02 | CAM-02 | CAMERA | Open Workspace North | NVR, Port 2 | 58 | PASS | PoE OK | Covers workspace toward core
03 | CAM-03 | CAMERA | Corridor | NVR, Port 3 | 55 | PASS | PoE OK | Looks down corridor to reception
04 | CAM-04 | CAMERA | Stair A | NVR, Port 4 | 57 | PASS | PoE OK | Stair door
05 | CAM-05 | CAMERA | IT / MDF | NVR, Port 5 | 31 | PASS | PoE OK | Rack room camera
06 | CAM-06 | CAMERA | Reception | NVR, Port 6 | 48 | PASS | PoE OK | Entry camera
07 | CAM-07 | CAMERA | Reception | NVR, Port 7 | 43 | FAIL | No PoE at camera end | Covers reception desk
08 | CAM-08 | CAMERA | Open Workspace South | NVR, Port 8 | 47 | PASS | PoE OK | Covers workspace from core
01 | COAX-01 | COAX | Conference (Hudson) | IT Room Rack B, Coax Splitter Port 1 | 95 | PASS |  | Display feed
02 | COAX-02 | COAX | Office 1 | IT Room Rack B, Coax Splitter Port 2 | 82 | FAIL | Dead | Abandoned TV outlet
03 | COAX-03 | COAX | Café | IT Room Rack B, Coax Splitter Port 3 | 64 | FAIL | Dead. No signal at TV | TV wall
04 | COAX-04 | COAX | Reception | IT Room Rack B, Coax Splitter Port 4 | 38 | PASS |  | Lobby TV, logo wall
05 | COAX-05 | COAX | Executive Office | IT Room Rack B, Coax Splitter Port 5 | 54 | FAIL | Dead | TV wall
06 | COAX-06 | COAX | Office 2 | IT Room Rack B, Coax Splitter Port 6 | 55 | PASS |  | TV wall
01 | DATA-01 | DATA | Conference (Hudson) | IT Room Rack A, PP1-01 | 89 | PASS | Cat6 certified | Wall plate behind display
02 | DATA-02 | DATA | Conference (Hudson) | IT Room Rack A, PP1-02 | 98 | FAIL | Shorted pair 3-6. Floor box damaged | Floor box under table
03 | DATA-03 | DATA | Conference (Hudson) | IT Room Rack A, PP1-03 | 84 | PASS | Cat6 certified | Wall plate, display wall
04 | DATA-04 | DATA | Office 1 | IT Room Rack A, PP1-04 | 92 | PASS |  | Desk wall
05 | DATA-05 | DATA | Office 1 | IT Room Rack A, PP1-05 | 78 | PASS | Continuity OK. Not terminated | Near door
06 | DATA-06 | DATA | Open Workspace North | IT Room Rack A, PP1-06 | 92 | PASS |  | Pod A
07 | DATA-07 | DATA | Open Workspace North | IT Room Rack A, PP1-07 | 78 | PASS |  | Pod A
08 | DATA-08 | DATA | Open Workspace North | IT Room Rack A, PP1-08 | 83 | PASS |  | Pod B
09 | DATA-09 | DATA | Open Workspace North | IT Room Rack A, PP1-09 | 74 | PASS |  | Pod B
10 | DATA-10 | DATA | Open Workspace North | IT Room Rack A, PP1-10 | 74 | FAIL | Open pair 4-5 | Pod C
11 | DATA-11 | DATA | Open Workspace North | IT Room Rack A, PP1-11 | 71 | FAIL | Not found at head-end | Pod C
12 | DATA-12 | DATA | Open Workspace North | IT Room Rack A, PP1-12 | 64 | PASS |  | Pod D
13 | DATA-13 | DATA | Open Workspace North | IT Room Rack A, PP1-13 | 56 | PASS |  | Pod D
14 | DATA-14 | DATA | Café | IT Room Rack A, PP1-14 | 69 | PASS |  | Counter, coffee machine telemetry
15 | DATA-15 | DATA | Reception | IT Room Rack A, PP1-15 | 41 | PASS | Cat6 certified | Access control reader, glass doors
16 | DATA-16 | DATA | Reception | IT Room Rack A, PP1-16 | 42 | PASS |  | Wall plate behind sofa
17 | DATA-17 | DATA | Reception | IT Room Rack A, PP1-17 | 46 | PASS |  | Reception desk
18 | DATA-18 | DATA | Open Workspace South | IT Room Rack A, PP1-18 | 55 | PASS |  | Pod E
19 | DATA-19 | DATA | Open Workspace South | IT Room Rack A, PP1-19 | 41 | PASS | Continuity OK. Not terminated | Between pods
20 | DATA-20 | DATA | Open Workspace South | IT Room Rack A, PP1-20 | 39 | FAIL | Split pair. Fails Cat6 | Pod F
21 | DATA-21 | DATA | Phone Booth 1 | IT Room Rack A, PP1-21 | 36 | PASS
22 | DATA-22 | DATA | Phone Booth 2 | IT Room Rack A, PP1-22 | 47 | UNTESTED | Booth locked. No access
23 | DATA-23 | DATA | Executive Office | IT Room Rack A, PP1-23 | 72 | PASS | Cat6 certified | Desk wall
24 | DATA-24 | DATA | Executive Office | IT Room Rack A, PP1-24 | 56 | PASS |  | Credenza
25 | DATA-25 | DATA | Office 2 | IT Room Rack A, PP1-25 | 62 | PASS |  | Desk wall
26 | DATA-26 | DATA | Office 2 | IT Room Rack A, PP1-26 | 54 | PASS |  | Window wall
01 | SPKR-01 | SPEAKER | Conference (Hudson) | IT Room Rack B, Amp Zone N | 101 | PASS |  | Ceiling speaker, left
02 | SPKR-02 | SPEAKER | Conference (Hudson) | IT Room Rack B, Amp Zone N | 90 | FAIL | Open circuit | Ceiling speaker, right
03 | SPKR-03 | SPEAKER | Open Workspace North | IT Room Rack B, Amp Zone N | 76 | PASS |  | Ceiling, paging zone N
04 | SPKR-04 | SPEAKER | Open Workspace North | IT Room Rack B, Amp Zone N | 68 | PASS |  | Ceiling, paging zone N
05 | SPKR-05 | SPEAKER | Café | IT Room Rack B, Amp Zone S | 53 | PASS |  | Ceiling
06 | SPKR-06 | SPEAKER | Reception | IT Room Rack B, Amp Zone S | 33 | PASS |  | Ceiling, background music
07 | SPKR-07 | SPEAKER | Open Workspace South | IT Room Rack B, Amp Zone S | 40 | PASS |  | Ceiling, paging zone S
08 | SPKR-08 | SPEAKER | Executive Office | IT Room Rack B, Amp Zone S | 58 | PASS |  | Ceiling
01 | TEL-01 | PHONE | Conference (Hudson) | 66 Block, Pair 1 | 104 | PASS |  | Conference phone
02 | TEL-02 | PHONE | Office 1 | 66 Block, Pair 2 | 91 | PASS
03 | TEL-03 | PHONE | Stair A | 66 Block, Pair 3 | 46 | PASS | Dial tone OK | Area of refuge phone
04 | TEL-04 | PHONE | Elevator | 66 Block, Pair 4 | 30 | PASS | Dial tone OK | Elevator emergency line
05 | TEL-05 | PHONE | Reception | 66 Block, Pair 5 | 38 | PASS |  | Reception desk
06 | TEL-06 | PHONE | Executive Office | 66 Block, Pair 6 | 72 | PASS
07 | TEL-07 | PHONE | Office 2 | 66 Block, Pair 7 | 46 | FAIL | No dial tone. Pair broken at 66 block
01 | UNK-01 | UNKNOWN | Open Workspace North |  | 69 | FAIL | Abandoned. Cut at ceiling | Unlabeled gray cable
02 | UNK-02 | UNKNOWN | ELEC |  |  | UNTESTED | Could not trace. Terminates in panel | Unlabeled, ELEC closet

## Head-End View
Head-End Logical View — Cables Grouped by Equipment
57 cables across all head-end equipment
Equipment | Count | Cable ID | Floor | Location | Port | Type
IT Room Rack A | 26 | DATA-01 | 7 | Conference (Hudson) | PP1-01 | DATA
|  | DATA-02 | 7 | Conference (Hudson) | PP1-02 | DATA
|  | DATA-03 | 7 | Conference (Hudson) | PP1-03 | DATA
|  | DATA-04 | 7 | Office 1 | PP1-04 | DATA
|  | DATA-05 | 7 | Office 1 | PP1-05 | DATA
|  | DATA-06 | 7 | Open Workspace North | PP1-06 | DATA
|  | DATA-07 | 7 | Open Workspace North | PP1-07 | DATA
|  | DATA-08 | 7 | Open Workspace North | PP1-08 | DATA
|  | DATA-09 | 7 | Open Workspace North | PP1-09 | DATA
|  | DATA-10 | 7 | Open Workspace North | PP1-10 | DATA
|  | DATA-11 | 7 | Open Workspace North | PP1-11 | DATA
|  | DATA-12 | 7 | Open Workspace North | PP1-12 | DATA
|  | DATA-13 | 7 | Open Workspace North | PP1-13 | DATA
|  | DATA-14 | 7 | Café | PP1-14 | DATA
|  | DATA-15 | 7 | Reception | PP1-15 | DATA
|  | DATA-16 | 7 | Reception | PP1-16 | DATA
|  | DATA-17 | 7 | Reception | PP1-17 | DATA
|  | DATA-18 | 7 | Open Workspace South | PP1-18 | DATA
|  | DATA-19 | 7 | Open Workspace South | PP1-19 | DATA
|  | DATA-20 | 7 | Open Workspace South | PP1-20 | DATA
|  | DATA-21 | 7 | Phone Booth 1 | PP1-21 | DATA
|  | DATA-22 | 7 | Phone Booth 2 | PP1-22 | DATA
|  | DATA-23 | 7 | Executive Office | PP1-23 | DATA
|  | DATA-24 | 7 | Executive Office | PP1-24 | DATA
|  | DATA-25 | 7 | Office 2 | PP1-25 | DATA
|  | DATA-26 | 7 | Office 2 | PP1-26 | DATA
IT Room Rack B | 14 | COAX-01 | 7 | Conference (Hudson) | Coax Splitter Port 1 | COAX
|  | COAX-02 | 7 | Office 1 | Coax Splitter Port 2 | COAX
|  | COAX-03 | 7 | Café | Coax Splitter Port 3 | COAX
|  | COAX-04 | 7 | Reception | Coax Splitter Port 4 | COAX
|  | COAX-05 | 7 | Executive Office | Coax Splitter Port 5 | COAX
|  | COAX-06 | 7 | Office 2 | Coax Splitter Port 6 | COAX
|  | SPKR-01 | 7 | Conference (Hudson) | Amp Zone N | SPEAKER
|  | SPKR-02 | 7 | Conference (Hudson) | Amp Zone N | SPEAKER
|  | SPKR-03 | 7 | Open Workspace North | Amp Zone N | SPEAKER
|  | SPKR-04 | 7 | Open Workspace North | Amp Zone N | SPEAKER
|  | SPKR-05 | 7 | Café | Amp Zone S | SPEAKER
|  | SPKR-06 | 7 | Reception | Amp Zone S | SPEAKER
|  | SPKR-07 | 7 | Open Workspace South | Amp Zone S | SPEAKER
|  | SPKR-08 | 7 | Executive Office | Amp Zone S | SPEAKER
NVR | 8 | CAM-01 | 7 | Open Workspace North | Port 1 | CAMERA
|  | CAM-02 | 7 | Open Workspace North | Port 2 | CAMERA
|  | CAM-03 | 7 | Corridor | Port 3 | CAMERA
|  | CAM-04 | 7 | Stair A | Port 4 | CAMERA
|  | CAM-05 | 7 | IT / MDF | Port 5 | CAMERA
|  | CAM-06 | 7 | Reception | Port 6 | CAMERA
|  | CAM-07 | 7 | Reception | Port 7 | CAMERA
|  | CAM-08 | 7 | Open Workspace South | Port 8 | CAMERA
66 Block | 7 | TEL-01 | 7 | Conference (Hudson) | Pair 1 | PHONE
|  | TEL-02 | 7 | Office 1 | Pair 2 | PHONE
|  | TEL-03 | 7 | Stair A | Pair 3 | PHONE
|  | TEL-04 | 7 | Elevator | Pair 4 | PHONE
|  | TEL-05 | 7 | Reception | Pair 5 | PHONE
|  | TEL-06 | 7 | Executive Office | Pair 6 | PHONE
|  | TEL-07 | 7 | Office 2 | Pair 7 | PHONE
(unassigned) | 2 | UNK-01 | 7 | Open Workspace North |  | UNKNOWN
|  | UNK-02 | 7 | ELEC |  | UNKNOWN